## Images (hidden)
Images
Recommended image size: 200 x 200 pixels. Format: png, with transparent background
Place an image in the cell. Size to 3.2 x 3.2 cm (1.25" x 1.25") maximum. Select the cell (not the image) and name it as "imgProduct".
Then, in the Image Name column on the Database (column I), just put "Product" name (without "img").
STICK | RSD | ENET | MIOM | IO1 | WIO
A2 | Sentinel | PressureScout | SFL-Rigid | SFL-Flex | WiomMini
FieldMonitor | NodeChecker | TiltScout | SFTotalizer | Totalizer | ModQ
DC-DC Converter | Battery 1B IS | Battery 3D | Battery 3D IS | Battery 3AA IS | Battery IQ
CBBL | USB-Serial | USB-4Pin | Antenna WHIP | Antenna EXT | Antenna
Compression | Repeater | SolarC1D1 | PowerPak | LCDCAL
None | DemoKit | LinkScout | GW V2 | GWv2+ANT | GWv2+EXT
STICK+CBBL | STICK+ENET | STICK+RSD | STICK+MIOM | STICK+IO1 | STICK+TOTALIZER
GWDin | GWDIN+ENET | GWDIN+MIOM | WIO+EXT | WIO+ANT | WIO+WHIP
WiomMini+EXT | WiomMini+ANT | WiomMini+WHIP | Bracket 5300 | Bracket Vega | Bracket Yokogawa
Ranger

## SolarPower
Solar Power System Sizing
» Input Values
Device / Configuration: |  | Gateway Stick - Standard
Power Supply: |  | 12 | System voltage |  |  |  | Print
Required Autonomy: |  | 5 | Days without sunlight
Min. Allowed Battery charge: |  | 25%
Hours to 100% charge: |  | 8 | Hours of sunlight to recover from 25% to 100% charge
#REF!
#REF!
#REF!
25%
|  | 5 |  |  | 8
» Results
| Average Current Draw: | 25 | from table
| Ah/Day: | 0.6 | Ah/Day
| Battery Capacity Needed: | 4 | Ah
| Charging Current Needed: | 0.375 | A
| Solar Panel Size: | 4.5 | W
Solar Panel
Charge controller
4.5
12
4
| Device | 25 |  | 0.375 | Battery
» Device consumption table
Device / Configuration |  |  | Avg. Current (mA)
|  |  | 12 | 24 |  | Image
Modbus Stick - None |  |  | 18 | 18 |  | Stick
RSD System (Stick and Module) - Both relays off |  |  | 18 | 12 |  | STICK_RSD
RSD System (Stick and Module) - One relay on |  |  | 34 | 22 |  | STICK_RSD
RSD System (Stick and Module) - Both relays on |  |  | 50 | 30 |  | STICK_RSD
Gateway Stick - Standard |  |  | 25 | 17 |  | Stick
Gateway Stick - With ENET Module |  |  | 85 | 57 |  | STICK_ENET
Gateway V2 (RS485 version) / No AI |  |  | 25 | 16 |  | GWv2
Gateway V2 (Ethernet / No AI |  |  | 85 | 50 |  | GWv2
MIOM (module only) - No relays on |  |  | 2 | 1.3 |  | MIOM
MIOM (module only) - 1 relay on |  |  | 9.6 | 5.8 |  | MIOM
MIOM (module only) - 2 relays on |  |  | 16.7 | 9.6 |  | MIOM
MIOM (module only) - 3 relays on |  |  | 24.3 | 13.6 |  | MIOM
MIOM (module only) - 4 relays on |  |  | 31.1 | 17 |  | MIOM
Modbus IO1 Module (module only) - Relay off |  |  | 3 |  |  | IO1
Modbus IO1 Module (module only) - Relay on |  |  | 10 |  |  | IO1
Wireless-IO Module - 15 sec check-in. No relays |  |  | 21.1 |  |  | WIO
Wireless-IO Module - 15 sec check-in. 1 relay |  |  | 36.5 |  |  | WIO
Wireless-IO Module - 15 sec check-in. 2 relays |  |  | 51.5 |  |  | WIO
WIOM Mini Module - 15 sec check-in. No relays / No AI |  |  | 25 |  |  | WIOMMini
WIOM Mini Module - 15 sec check-in. 1 relay / No AI |  |  | 40 |  |  | WIOMMini
WIOM Mini Module - 15 sec check-in. 2 relays / No AI |  |  | 55 |  |  | WIOMMini
Stick

## NodeCalc
Packets per minute calculator
» Input Values
Fill out the number of remote nodes at each check-in interval connected to the gateway.
The packets per minute should be 60 or less for ideal communications. | [5 empty] | Print
| Check-in Interval | Nodes | Packets per min. |  | % of traffic
| 5 seconds | 2 | 24 |  | 56.69%
| 15 seconds | 3 | 12 |  | 28.35%
| 1 minute | 5 | 5 |  | 11.81%
| 2 minutes | 0 | 0 |  | 0%
| 4.5 minutes | 6 | 1.3333 |  | 3.15%
| 10 minutes | 0 | 0 |  | 0%
| 15 minutes | 0 | 0 |  | 0%
| 30 minutes | 0 | 0 |  | 0%
| 60 minutes | 0 | 0 |  | 0%
» Results
| Nodes: |  | 16 | Nodes OK.
| Packets per minute: |  | 42.3333 | Packets per min. OK.
Traffic distribution according to check-in interval