## Dev1
SignalFire Ranger Tag Guide: Firmware Revision v0.1.45-airq - Tag Names will not change in future firmware revisions
Tag Name | Alias | DataType | Writable | Part of periodic report | Report on change | Units | Low Range | High Range | Default | Tag Description
bdSeq | 0 | UINT32 | No | No | No |  |  |  |  | Implemented as per SparkPlug specification. Counts the number of MQTT connections over the life of the device.
Node Control/Reboot | 1 | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to reboot.
Node Control/Rebirth |  | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to resend SparkPlug BIRTH information. (NOTE: Does not disconnect from MQTT broker.)
Node Control/Next Server | 3 | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to disconnect from the current MQTT broker, and connect to the next configured broker.
Node Control/Group ID | 4 | STRING | Yes | No | No |  |  |  | none | Writing to this changes the group_id within the SparkPlug MQTT topic namespace the Ranger will use to communicate. See section 6.1 "Sparkplug Topic Namespace Elements" of the SparkPlug spec for more details
Properties/HW Rev | 5 | STRING | No | No | No |  |  |  |  | Reports a string identifying the make and model of hardware. Will be "SignalFire Ranger (v2)".
Properties/HW Config | 6 | STRING | No | No | No |  |  |  | AIRQ | Reports a string which identifies factory hardware configuration of the node. "AIRQ" indicates Ranger AirQ with built-in gas sensor.
Properties/SW Rev | 7 | STRING | Yes | No | No |  |  |  |  | Reports a string identifying the firmware version running on the Ranger. Firmware-over-the-air updates can be triggered by writing the full URL or relative path to the firmware .fwi file to download. See Ranger Private Cloud OTA Firmware Update Process application note.
Properties/Name | 8 | STRING | Yes | No | Yes |  |  |  |  | Reports a customizable name for this Ranger node. This is purely informational and can be modified at will by the customer by writing to the tag.
Properties/Report Interval | 9 | UINT32 | Yes | No | Yes | s | 5 | 43200 | 900 | The interval between periodic reports. Writing any value to this tag configures the interval and also triggers an immediate sensor check and report. Rewriting the current tag value, if allowed, or writing a value of 0, both trigger an immediate periodic report.
Console | 10 | STRING | Yes | No | No |  |  |  |  | Used for remote debug/support of the Ranger node.
Temperature | 11 | FLOAT | No | Yes | No | °C | -40 | 125 |  | Reports the current electronics temperature of the cellular modem.
Battery | 12 | FLOAT | No | Yes | No | V | 0 | 5 |  | Reports the voltage of the battery, sampled during reports while sensor is powered on.
Connect Time | 13 | DATETIME | No | No | No |  |  |  |  | Timestamp of when the Ranger most recently connected to the MQTT broker, given as milliseconds since January 1, 1970 UTC
Local UTC Offset | 14 | INT16 | No | No | No | minutes | -720 | 840 |  | Local timezone offset from UTC at the Ranger's location, as reported to it by the cellular network.
Feature Flags | 15 | UINT32 | Yes | No | Yes |  |  |  | 0 | Optional Feature Flags that enable or disable certain functionality or operations of the device.
Feature Flag 4 - bit3 (0x08) - Disable Low Power LTE-M/NB-IoT Features (eDRX). This is also referred to as Low Latency Mode.
Feature Flag 5 - bit4 (0x10) - Metric Write-Protection Enabled. This feature flag is read-only, and cannot be set by writing the Feature Flags.
Subscription | 16 | STRING | Yes | No | Yes |  |  |  | RPT60 | Subscription (SignalFire Cloud internal use)
GNSS/Active | 17 | BOOLEAN | Yes | No | Yes |  |  |  |  | Reports if the GNSS subsystem is currently active and trying to get a fix. Writing 1 or 0 to this tag will immediately enable or disable the GNSS receiver.
GNSS/Interval | 18 | UINT32 | Yes | No | Yes | s | 0 | 64800 | 0 | Controls the amount of time between automatic GNSS location fixes. Setting this to 0 disables automatic fixes.
GNSS/Timeout | 19 | UINT32 | Yes | No | Yes | s | 0 | 600 | 300 | Controls the amount of time the Ranger will try to get a GNSS fix before giving up.
GNSS/NMEA | 20 | STRING | No | No | Yes |  |  |  |  | NMEA string from the most recent GNSS fix.
GNSS/Timestamp | 21 | DATETIME | No | No | Yes |  |  |  |  | Timestamp of the most recent GNSS fix, given as milliseconds since January 1, 1970 UTC
GNSS/Latitude | 22 | DOUBLE | No | No | Yes |  |  |  | 0 | The latitude of the most recent GNSS fix, in degrees.
GNSS/Longitude | 23 | DOUBLE | No | No | Yes |  |  |  | 0 | The longitude of the most recent GNSS fix, in degrees.
Modem/IMEI | 24 | STRING | No | No | No |  |  |  |  | Reports the International Mobile Equipment Identity (IMEI) of the modem.
Modem/ICCID | 25 | STRING | No | No | No |  |  |  |  | Reports the Integrated Circuit Card Identification (ICCID) number of the SIM card.
Modem/Rev | 26 | STRING | No | No | No |  |  |  |  | Reports a string identifying the firmware version running on the cellular modem.
Modem/Console | 27 | STRING | Yes | No | No |  |  |  |  | Used for remote debug/support of the Ranger node.
Modem/Connect Delay | 28 | UINT32 | No | No | No | ms |  |  |  | Reports how many milliseconds the cellular modem took to fully register with a cell tower for the most recent offline-to-online transition
Modem/Band | 29 | UINT8 | No | Yes | No |  |  |  |  | Reports the modem frequency band in use.
Modem/RSRP | 30 | INT16 | No | Yes | No | dBm | -140 | -44 |  | Reports strength of the cellular signal as received by the modem, specifically the Reference Signal Received Power (RSRP)
Modem/RSRQ | 31 | FLOAT | No | Yes | No | dB | -19.5 | -3 |  | Reports quality of the cellular signal as received by the modem, specifically the Reference Signal Received Quality (RSRQ)
Modem/Roaming | 32 | BOOLEAN | No | Yes | No |  |  |  |  | Reports if the cellular service in use is considered "roaming" by the SIM card.
Modem/CEREG/CI | 33 | STRING | No | Yes | No |  |  |  |  | Reports the E-UTRAN cell ID of the current cellular service in use.
Modem/CEREG/TAC | 34 | STRING | No | Yes | No |  |  |  |  | Reports the Tracking Area Code (TAC) of the current cellular service in use.
Modem/CEREG/ACT | 35 | UINT8 | No | No | No |  |  |  |  | Reports the activation type of the current cellular service in use. (7=LTE-M1, 9=NB-IoT)
Modem/Operator | 36 | STRING | No | No | Yes |  |  |  |  | Reports the name of the current cellular operator in use, as reported by the cellular tower
Modem/MCCMNC | 37 | STRING | No | No | Yes |  |  |  |  | Reports the mobile country code and mobile network code (MCCMNC) of the current cellular service in use
Modem/eDRX | 38 | STRING | No | Yes | No | s |  |  |  | Reports the LTE-M or NB-IoT extended discontinuous reception (eDRX) interval, in seconds, "Disabled", or "Not Provided"
Mgmt/CertUploadCA | 39 | STRING | Yes | No | Yes |  |  |  |  | Reports the state and byte count of the staged CA Certificate, or a blank string when Idle. Writing to this stages the new CA Certificate file, in PEM format, to be installed and activated.
Mgmt/CertUploadPublic | 40 | STRING | Yes | No | Yes |  |  |  |  | Reports the state and byte count of the staged Public Certificate, or a blank string when Idle. Writing to this stages the new Public Certificate file, in PEM format, to be installed and activated.
Mgmt/CertUploadKey | 41 | STRING | Yes | No | Yes |  |  |  |  | Reports the state and byte count of the staged Private Key, or a blank string when Idle. Writing to this stages the new Private Key file, in PEM format, to be installed and activated.
Mgmt/CertCommand | 42 | STRING | Yes | No | Yes |  |  |  |  | Reports the status or error message of the most recent command. Writing "activate" or "clear" to this commands the staged certificate and key files to be activated (after reboot) or cleared (without rebooting).
Dev1/Report Count | 43 | UINT32 | No | Yes | No |  |  |  |  | Counts the number of periodic reports that have been generated. Useful for examining report history and determining when reports were generated and where data might be missing.
Dev1/Fast Reporting/Active | 44 | BOOLEAN | No | No | Yes |  |  |  |  | Reports if Fast Reporting Mode is currently active.
Dev1/Fast Reporting/Enabled | 45 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Controls whether Fast Reporting Mode is enabled or disabled. Disabling Fast Report Mode while it is active will immediately end Fast Reporting.
Dev1/Fast Reporting/Report Interval | 46 | UINT32 | Yes | No | Yes | s | 5 | 43200 | Properties/Report Interval | The Report Interval to use in Fast Reporting Mode. See the "Properties/Report Interval" tag.
Dev1/Fast Reporting/Mode | 47 | STRING | Yes | No | Yes |  |  |  | Until Cleared | The Fast Reporting Mode control logic for stay in Fast Reporting Mode once it is active. Options are "Until Cleared" or "Duration"
Dev1/Fast Reporting/Duration | 48 | UINT32 | Yes | No | Yes | s | 5 | 43200 | 3600 | The duration to stay in Fast Reporting Mode once triggered, if the Fast Report Mode is set to "Duration"
Dev1/Fast Reporting/Condition | 49 | STRING | Yes | No | Yes |  |  |  | Any | The Fast Reporting condition to use when evaluating the Fast Report Triggers. Options are "Any" or "All" triggers evaluating TRUE to enter Fast Reporting Mode.
Dev1/Fast Reporting/Triggers | 50 | STRING | Yes | No | Yes |  |  |  |  | Defines the Fast Reporting Triggers, in CSV format. Up to 4 Fast Reporting Trigger rows can be defined. See 'CSV Formatting' sheet

## DevAirQ
SignalFire Ranger Tag Guide: Firmware Revision v0.1.45-airq - Tag Names will not change in future firmware revisions
Tag Name | Alias | DataType | Writable | Part of periodic report | Report on change | Units | Low Range | High Range | Default | Description
Sensor Type | 51 | UINT8 | No | Yes | No |  |  |  |  | Sensor Type: Methane Sensor (0x05), Flammable Gas Sensor (0x03)
Concentration | 52 | FLOAT | No | Yes | No | ppm or %LEL |  |  |  | Gas concentration: Methane Sensor in ppm, Flammable Gas Sensor in %LEL
Gas ID | 53 | UINT32 | No | Yes | No |  |  |  |  | The Gas ID:
0 = No Gas
1 = Hydrogen
2 = Hydrogen Mixture (*Flammable Gas Sensor Only)
3= Methane Sensor: Methane/Natural Gas Flammable Gas Sensor: Methane
4 = Light Gas (*Flammable Gas Sensor Only)
5 = Medium Gas (*Flammable Gas Sensor Only)
6 = Heavy Gas (*Flammable Gas Sensor Only)
253 = Unknown Gas
254 = Under Range, Under Range - Concentration less than -5 %LEL (*Flammable Gas Sensor Only)
255 = Methane Sensor: Over Range, Concentration greater than 1,100,000 ppm Flammable Gas Sensor: Over Range, Concentration greater than or equal to 110 %LEL
Absolute Humidity | 54 | FLOAT | No | Yes | No | g/m3 |  |  |  | Ambient absolute humidity, in g/m3
Relative Humidity | 55 | FLOAT | No | Yes | No | %RH |  |  |  | Ambient relative humidity, in %RH
Temperature | 56 | FLOAT | No | Yes | No | °C |  |  |  | Ambient temperature, in °C
Pressure | 57 | FLOAT | No | Yes | No | kPa |  |  |  | Ambient pressure, in kPa
Tilt | 58 | BOOLEAN | No | Yes | Yes |  |  |  |  | Tilt State, 0 = Not Tilted, 1 = Tilted
Sensor Status | 59 | UINT8 | No | Yes | No |  |  |  |  | The Gas sensor status byte:
0x00 = OK - Gas sensor is operating normally and has no errors
0x01 = CRC_FAILED - Transmitted data failed checksum
0x02 = BAR_PARAM - Illegal or bad parameters specified
0x03 = EXE_FAILED - Execution of command failed
0x04 = NO_MEM - Insufficient memory for operation
0x05 = UNKNOWN_CMD - Unknown Command ID specified
0x07 = INCOMPLETE_COMMAND - Incomplete or truncated command
0x21 = HW_ERR_VDD - Internal voltage out of range
0x22 = HW_ERR_VREF - Voltage out of range
0x23 = HW_ENV_XCD_RANGE - Environmental (Temp., Press., Humid.) out of range (*Flammable Gas Sensor Only)
0x24 = HW_ENV_SNSR_MALFUNCTION - Environmental sensor malfunction
0x25 = HW_ERR_MCU - Microcontroller error
0x26 = HW_SENSOR_INITIALIZATION - Sensor in initialization mode
0x27 = SENSOR_STARTUP - Sensor in start-up mode. No zeroing performed. (*Flammable Gas Sensor Only)
0x30 = SENSOR_NEGATIVE - Sensor output <-15%LEL; accuracy affected if flammable gas initially detected while in this condition (*Flammable Gas Sensor Only)
0x31 = CONDENSATION_DETECTED - Condensation condition exists at sensor (out of specification) (*Flammable Gas Sensor Only)
0x32 = HW_SENSOR_MALFUNCTION - Gas sensing element malfunction
0x33 = GAS_DETECTED_DURING_STARTUP - Sensor has detected flammable gas during start-up period (*Flammable Gas Sensor Only)
0x34 = SLOW_GAS_ACCUM_DETECTED - Sensor has detected a slow accumulation of gas (*Flammable Gas Sensor Only)
0x35 = BREATH_OR_HUMIDITY_SURGE - Sensor has detected condition indicative of human breath or humidity surge (*Flammable Gas Sensor Only)
0x80 = COMM_TIMEOUT - Sensor communication timeout
Config/Sampling Time | 60 | FLOAT | Yes | No | Yes | s | -1 | 3600 | 300 | The Gas sensor sampling time, in seconds. A value of -1 sets Continous Monitoring mode, and a value 300 to 3600 seconds sets Emissions Monitoring mode's periodic sensor sampling time.

## properties
SignalFire Ranger Tag Guide: Firmware Revision v0.1.45-airq - Property Names will not change in future firmware revisions
Property Name | DataType | Part of periodic report | Rebirth on change | Description
engLow | INT32 or FLOAT | No | Yes | Tag engineering low range value
engHigh | INT32 or FLOAT | No | Yes | Tag engineering high range value
engUnit | STRING | No | Yes | Tag engineering units string
Quality | INT32 | Yes | No | Tag quality (error status):
192 = Good
-2147483136 = Bad
-1073741048 = Error, Communication Fault (Status 0x01 - 0x07)
-1073741049 = Error, Timeout Expired
-1073741050 = Error, Communication I/O
-1073741056 = Error, Unspecified

## CSV Formatting
SignalFire Ranger Tag Guide: Firmware Revision v0.1.45-airq - CSV Formatting Guide
Comma Separated Variable (CSV) format is used for STRING tags that contain tabular data. These CSV strings use the Ignition 8.1 CSV File Format (link below). All columns use string (str) types, and rows can use either Windows (CR) or Unix (CR LF) as a Newline character.
Ignition 8.1 CSV File Format
Fast Reporting CSV Format (0 to 4 Rows)
#NAMES tagPath,comparator,threshold #TYPES str,str,str #ROWS,0
#NAMES | #TYPES | Required | Description
tagPath | str | Yes | Tag Path (Ex. Dev1/PRESS1)
comparator | str | Yes | Comparator used to compare tag value to trigger threshold. (>, <, or =)
threshold | str | Yes | Trigger threshold, as a decimal string
Example Trigger Fast Reporting when PRESS1 Maximum > 20.0 Trigger Fast Reporting when PRESS1 Average > 12.0
Example Formatted CSV String #NAMES tagPath,comparator,threshold #TYPES str,str,str #ROWS,2 DevMPS/Concentration,>,1000.000000