## Dev1
SignalFire Ranger Tag Guide: Firmware Revision v0.1.46-3v - Tag Names will not change in future firmware revisions
Tag Name | Alias | DataType | Writable | Part of periodic report | Report on change | Units | Low Range | High Range | Default | Tag Description
bdSeq | 0 | UINT32 | No | No | No |  |  |  |  | Implemented as per SparkPlug specification. Counts the number of MQTT connections over the life of the device.
Node Control/Reboot | 1 | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to reboot.
Node Control/Rebirth |  | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to resend SparkPlug BIRTH information. (NOTE: Does not disconnect from MQTT broker.)
Node Control/Next Server | 3 | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to disconnect from the current MQTT broker, and connect to the next configured broker.
Node Control/Group ID | 4 | STRING | Yes | No | No |  |  |  | none | Writing to this changes the group_id within the SparkPlug MQTT topic namespace the Ranger will use to communicate. See section 6.1 "Sparkplug Topic Namespace Elements" of the SparkPlug spec for more details
Properties/HW Rev | 5 | STRING | No | No | No |  |  |  |  | Reports a string identifying the make and model of hardware. Will be "SignalFire Ranger (v1)" or "SignalFire Ranger (v2)".
Properties/HW Config | 6 | STRING | No | No | No |  |  |  | 3V | Reports a string which identifies factory hardware configuration of the node. "3V" indicates built-in 3.3V pressure sensor.
Properties/SW Rev | 7 | STRING | Yes | No | No |  |  |  |  | Reports a string identifying the firmware version running on the Ranger. Firmware-over-the-air updates can be triggered by writing the full URL or relative path to the firmware .fwi file to download. See Ranger Private Cloud OTA Firmware Update Process application note.
Properties/Name | 8 | STRING | Yes | No | Yes |  |  |  |  | Reports a customizable name for this Ranger node. This is purely informational and can be modified at will by the customer by writing to the tag.
Properties/Report Interval | 9 | UINT32 | Yes | No | Yes | s | 5 | 43200 | 300 | The interval between periodic reports. Writing any value to this tag configures the interval and also triggers an immediate sensor check and report. Rewriting the current value is the recommended method to trigger an immediate periodic report.
Console | 10 | STRING | Yes | No | No |  |  |  |  | Used for remote debug/support of the Ranger node.
Temperature | 11 | FLOAT | No | Yes | No | °C | -40 | 125 |  | Reports the current electronics temperature of the cellular modem.
Battery | 12 | FLOAT | No | Yes | No | V | 0 | 5 |  | Reports the voltage of the battery, sampled during reports while sensor is powered on.
Connect Time | 13 | DATETIME | No | No | No |  |  |  |  | Timestamp of when the Ranger most recently connected to the MQTT broker, given as milliseconds since January 1, 1970 UTC
Local UTC Offset | 14 | INT16 | No | No | No | minutes | -720 | 840 |  | Local timezone offset from UTC at the Ranger's location, as reported to it by the cellular network.
Feature Flags | 15 | UINT32 | Yes | No | Yes |  |  |  | 0 | Optional Feature Flags that enable or disable certain functionality or operations of the device.
Feature Flag 4 - bit3 (0x08) - Disable Low Power LTE-M/NB-IoT Features (eDRX). This is also referred to as Low Latency Mode.
Feature Flag 5 - bit4 (0x10) - Metric Write-Protection Enabled. This feature flag is read-only, and cannot be set by writing the Feature Flags.
Subscription | 16 | STRING | Yes | No | Yes |  |  |  | RPT60 | Subscription (SignalFire Cloud internal use)
GNSS/Active | 17 | BOOLEAN | Yes | No | Yes |  |  |  |  | Reports if the GNSS subsystem is currently active and trying to get a fix. Writing 1 or 0 to this tag will immediately enable or disable the GNSS receiver.
GNSS/Interval | 18 | UINT32 | Yes | No | Yes | s | 0 | 64800 | 0 | Controls the amount of time between automatic GNSS location fixes. Setting this to 0 disables automatic fixes.
GNSS/Timeout | 19 | UINT32 | Yes | No | Yes | s | 0 | 600 | 300 | Controls the amount of time the Ranger will try to get a GNSS fix before giving up.
GNSS/NMEA | 20 | STRING | No | No | Yes |  |  |  |  | NMEA string from the most recent GNSS fix.
GNSS/Timestamp | 21 | DATETIME | No | No | Yes |  |  |  |  | Timestamp of the most recent GNSS fix, given as milliseconds since January 1, 1970 UTC
GNSS/Latitude | 22 | DOUBLE | No | No | Yes |  |  |  | 0 | The latitude of the most recent GNSS fix, in degrees.
GNSS/Longitude | 23 | DOUBLE | No | No | Yes |  |  |  | 0 | The longitude of the most recent GNSS fix, in degrees.
Modem/IMEI | 24 | STRING | No | No | No |  |  |  |  | Reports the International Mobile Equipment Identity (IMEI) of the modem.
Modem/ICCID | 25 | STRING | No | No | No |  |  |  |  | Reports the Integrated Circuit Card Identification (ICCID) number of the SIM card.
Modem/Rev | 26 | STRING | No | No | No |  |  |  |  | Reports a string identifying the firmware version running on the cellular modem.
Modem/Console | 27 | STRING | Yes | No | No |  |  |  |  | Used for remote debug/support of the Ranger node.
Modem/Connect Delay | 28 | UINT32 | No | No | No | ms |  |  |  | Reports how many milliseconds the cellular modem took to fully register with a cell tower for the most recent offline-to-online transition
Modem/Band | 29 | UINT8 | No | Yes | No |  |  |  |  | Reports the modem frequency band in use.
Modem/RSRP | 30 | INT16 | No | Yes | No | dBm | -140 | -44 |  | Reports strength of the cellular signal as received by the modem, specifically the Reference Signal Received Power (RSRP)
Modem/RSRQ | 31 | FLOAT | No | Yes | No | dB | -19.5 | -3 |  | Reports quality of the cellular signal as received by the modem, specifically the Reference Signal Received Quality (RSRQ)
Modem/Roaming | 32 | BOOLEAN | No | Yes | No |  |  |  |  | Reports if the cellular service in use is considered "roaming" by the SIM card.
Modem/CEREG/CI | 33 | STRING | No | Yes | No |  |  |  |  | Reports the E-UTRAN cell ID of the current cellular service in use.
Modem/CEREG/TAC | 34 | STRING | No | Yes | No |  |  |  |  | Reports the Tracking Area Code (TAC) of the current cellular service in use.
Modem/CEREG/ACT | 35 | UINT8 | No | No | No |  |  |  |  | Reports the activation type of the current cellular service in use. (7=LTE-M1, 9=NB-IoT)
Modem/Operator | 36 | STRING | No | No | Yes |  |  |  |  | Reports the name of the current cellular operator in use, as reported by the cellular tower
Modem/MCCMNC | 37 | STRING | No | No | Yes |  |  |  |  | Reports the mobile country code and mobile network code (MCCMNC) of the current cellular service in use
Modem/eDRX | 38 | STRING | No | Yes | No | s |  |  |  | Reports the LTE-M or NB-IoT extended discontinuous reception (eDRX) interval, in seconds, "Disabled", or "Not Provided"
Mgmt/CertUploadCA | 39 | STRING | Yes | No | Yes |  |  |  |  | Reports the state and byte count of the staged CA Certificate, or a blank string when Idle. Writing to this stages the new CA Certificate file, in PEM format, to be installed and activated.
Mgmt/CertUploadPublic | 40 | STRING | Yes | No | Yes |  |  |  |  | Reports the state and byte count of the staged Public Certificate, or a blank string when Idle. Writing to this stages the new Public Certificate file, in PEM format, to be installed and activated.
Mgmt/CertUploadKey | 41 | STRING | Yes | No | Yes |  |  |  |  | Reports the state and byte count of the staged Private Key, or a blank string when Idle. Writing to this stages the new Private Key file, in PEM format, to be installed and activated.
Mgmt/CertCommand | 42 | STRING | Yes | No | Yes |  |  |  |  | Reports the status or error message of the most recent command. Writing "activate" or "clear" to this commands the staged certificate and key files to be activated (after reboot) or cleared (without rebooting).
Dev1/Report Count | 43 | UINT32 | No | Yes | No |  |  |  |  | Counts the number of periodic reports that have been generated. Useful for examining report history and determining when reports were generated and where data might be missing.
Dev1/PRESS1 | 44 | FLOAT | Yes | Yes | No | Configurable |  |  |  | Reports the current pressure reading of PRESS1, scaled to the span of the pressure sensor and converted to the pressure units. If using Custom Pressure Units, PRESS1 is scaled between Scale Low and Scale High. Writing to this tag zeroes PRESS1 to the pressure value written.
Dev1/PRESS1 Raw | 45 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the current analog reading or PRESS1. This value is before the scaling, and will be reported as a value in Volts or milliamps, depending on the position of the Analog IN Select switch on the Ranger.
Dev1/PRESS1 Config/Scale Low | 46 | FLOAT | Yes | No | Yes |  |  |  | 0 | The lower range value to use when scaling PRESS1, if using Custom Pressure Units.
Dev1/PRESS1 Config/Scale High | 47 | FLOAT | Yes | No | Yes |  |  |  | 0 | The upper range value to use when scaling PRESS1, if using Custom Pressure Units.
Dev1/PRESS1 Config/Scale Adjust | 48 | FLOAT | Yes | No | Yes |  |  |  | 0 | The +/- adjustment to use when scaling PRESS1.
Dev1/PRESS1 Config/Scale Units | 49 | STRING | Yes | No | Yes |  |  |  |  | The PRESS1 scaled units description, if using Custom Pressure Units.
Dev1/PRESS1 Config/Sensor On Time | 50 | FLOAT | No | No | Yes | s | 0 | 120 | 0.09 | The time duration to enable sensor power before sampling PRESS1. A value of 0 disables sensor power.
Dev1/PRESS1 Config/Sampling Interval | 51 | FLOAT | Yes | No | Yes | s | 0 | 3600 | 0 | The interval between PRESS1 pressure sensor samples. Set to 0 to disable sampling between reports, and only sample on the Report Interval.
Dev1/PRESS1 Config/Specific Gravity | 52 | FLOAT | Yes | No | Yes |  |  |  | 1 | The specific gravity to divide the PRESS1 pressure sensor reading by, in applications reading liquid level from the pressure sensor.
Dev1/PRESS1 Config/Low Alarm | 53 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Enables or disables the Low Alarm on PRESS1.
Dev1/PRESS1 Config/Low Threshold | 54 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The low pressure threshold for the Low Alarm on PRESS1.
Dev1/PRESS1 Config/High Alarm | 55 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Enables or disables the High Alarm on PRESS1.
Dev1/PRESS1 Config/High Threshold | 56 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The high pressure threshold for the High Alarm on PRESS1.
Dev1/PRESS1 Config/Zero Offset | 57 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The calibrated zero offset for PRESS1. Writing 0 to this tag clears the zero offset for PRESS1.
Dev1/PRESS1 Minimum | 58 | FLOAT | No | Yes | No | Configurable |  |  |  | The minimum PRESS1 pressure sensor sample taken this report interval
Dev1/PRESS1 Maximum | 59 | FLOAT | No | Yes | No | Configurable |  |  |  | The maximum PRESS1 pressure sensor sample taken this report interval
Dev1/PRESS1 Average | 60 | FLOAT | No | Yes | No | Configurable |  |  |  | The average of all PRESS1 pressure sensor samples taken this report interval
Dev1/PRESS1 Config/Pressure Span | 61 | UINT32 | No | No | Yes | psi |  |  | 0 | The span of the pressure sensor, in psi.
Dev1/PRESS1 Config/Pressure Units | 62 | STRING | Yes | No | Yes | Configurable |  |  | psi | The pressure units to convert the raw pressure sensor reading to (psi, bar, kPa, inH₂O, ftH₂O, oz/in², Custom)
Dev1/Fast Reporting/Active | 63 | BOOLEAN | No | No | Yes |  |  |  |  | Reports if Fast Reporting Mode is currently active.
Dev1/Fast Reporting/Enabled | 64 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Controls whether Fast Reporting Mode is enabled or disabled. Disabling Fast Report Mode while it is active will immediately end Fast Reporting.
Dev1/Fast Reporting/Report Interval | 65 | UINT32 | Yes | No | Yes | s | 5 | 43200 | Properties/Report Interval | The Report Interval to use in Fast Reporting Mode. See the "Properties/Report Interval" tag.
Dev1/Fast Reporting/Sensor On Time | 66 | FLOAT | No | No | Yes | s | 0 | 120 | Dev1/PRESS1 Config/Sensor On Time | The Sensor On Time to use in Fast Reporting Mode. See the "Dev1/PRESS1 Config/Sensor On Time" tag.
Dev1/Fast Reporting/Mode | 67 | STRING | Yes | No | Yes |  |  |  | Until Cleared | The Fast Reporting Mode control logic for stay in Fast Reporting Mode once it is active. Options are "Until Cleared" or "Duration"
Dev1/Fast Reporting/Duration | 68 | UINT32 | Yes | No | Yes | s | 5 | 43200 | 3600 | The duration to stay in Fast Reporting Mode once triggered, if the Fast Report Mode is set to "Duration"
Dev1/Fast Reporting/Condition | 69 | STRING | Yes | No | Yes |  |  |  | Any | The Fast Reporting condition to use when evaluating the Fast Report Triggers. Options are "Any" or "All" triggers evaluating TRUE to enter Fast Reporting Mode.
Dev1/Fast Reporting/Triggers | 70 | STRING | Yes | No | Yes |  |  |  |  | Defines the Fast Reporting Triggers, in CSV format. Up to 4 Fast Reporting Trigger rows can be defined. See 'CSV Formatting' sheet
Dev1/Strapping Config/Chart | 71 | STRING | Yes | No | Yes |  |  |  |  | The Strapping Chart to apply, in CSV format, up to 128 lines
Dev1/Strapping Config/Tag | 72 | STRING | Yes | No | Yes |  |  |  |  | The Tag Name to use when applying the strapping chart
Dev1/Strapping Value | 73 | FLOAT | No | Yes | No |  |  |  |  | Output value from the Strapping Chart calculation
Dev1/Strapping Config/Unit | 74 | STRING | Yes | No | Yes |  |  |  |  | The units string to report with the Strapping Value

## properties
SignalFire Ranger Tag Guide: Firmware Revision v0.1.46-3v - Property Names will not change in future firmware revisions
Property Name | DataType | Part of periodic report | Rebirth on change | Description
engLow | INT32 or FLOAT | No | Yes | Tag engineering low range value
engHigh | INT32 or FLOAT | No | Yes | Tag engineering high range value
engUnit | STRING | No | Yes | Tag engineering units string

## CSV Formatting
SignalFire Ranger Tag Guide: Firmware Revision v0.1.46-3v - CSV Formatting Guide
Comma Separated Variable (CSV) format is used for STRING tags that contain tabular data. These CSV strings use the Ignition 8.1 CSV File Format (link below). All columns use string (str) types, and rows can use either Windows (CR) or Unix (CR LF) as a Newline character.
Ignition 8.1 CSV File Format
Fast Reporting CSV Format (0 to 4 Rows)
#NAMES tagPath,comparator,threshold #TYPES str,str,str #ROWS,0
#NAMES | #TYPES | Required | Description
tagPath | str | Yes | Tag Path (Ex. Dev1/PRESS1)
comparator | str | Yes | Comparator used to compare tag value to trigger threshold. (>, <, or =)
threshold | str | Yes | Trigger threshold, as a decimal string
Example Trigger Fast Reporting when PRESS1 Maximum > 20.0 Trigger Fast Reporting when PRESS1 Average > 12.0
Example Formatted CSV String #NAMES tagPath,comparator,threshold #TYPES str,str,str #ROWS,2 Dev1/PRESS1 Maximum,>,20.000000 Dev1/PRESS1 Average,>,12.000000